## Virginia_11541
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number | 11541 | 11541 | 11541 | Registration No. 11541
Permit Issuance Date | 2008-05-16 00:00:00 | 2008-05-16 | 2008-05-16 | 2008-05-16
Permit Expiration Date
Facility Name | Southwest Enterprise Solutions Center | the Southwest Enterprise Solutions Center | Corporate Office Properties, LP | the Southwest Enterprise Solutions Center
Facility Address | Technology Park Drive, at the Regional Business Technology Park in Lebanon, Russell County, Virginia | Technology Park Drive, at the Regional Business Technology Park in Lebanon, Russell County, Virginia | Technology Park Drive, Regional Business Technology Park, Lebanon, Russell County, VA | Technology Park Drive, at the Regional Business Technology Park in Lebanon, Russell County, Virginia
Facility County | Russel County | Russell County | Russell County | Russell County
Facility State |  | VA |  | VA
Construction Notification Required |  | Yes |  | Yes
Construction Notification Window (Days) |  | 30 |  | 30
Startup Notification Required |  | Yes |  | Yes
Startup Notification Window (Days) |  | 15 |  | 16
Permit Copy Onsite Required |  | Yes |  | Yes
Right of Entry Clause |  | The permittee shall allow authorized local, state, and federal representatives, upon the presentation of credentials: a. To enter upon the permittee's premises on which the facility is located or in which any records are required to be kept under the terms and conditions of this permit; b. To have access to and copy at reasonable times any records required to be kept under the terms and conditions of this permit or the State Air Pollution Control Board Regulations; c. To inspect at reasonable ti... |  | 12. R2btotEntryThepermitteeshall allow authonzed local, state, and federal representatives, upon the presentation of credentials: a. Toenter upon the permittee's premises on which the facility is located or in which any records are required to be kept underthe terms and conditions ofthis permit; b Tohave access to and copy at reasonable times any records required to be kept underthe terms and conditions ofthis permit orthe State Air Pollution Control Board Regulations; c. Toinspect at reasonable...
GENERATOR SET 1
Reference Number | 3 | 3 | 3 | Ref No. 3
Number of Generators | 1 | 1 | 1 | 1
Included in Project |  | Yes |  | Yes
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model |  |  | 1500 kW diesel-powered emergency generator
Rated Capacity (kW) | 1500 | 1500 | 1500 | 1500
Rated Capacity (BHP) |  | 2500 | 2500 | 2500
Rated Capacity (HP) | 2500
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Distillate oil | distillate oil | distillate oil | distillate oil
Secondary Fuel Type
Fuel Grade | 1 or 2 | numbers 1 or 2 fuel oil |  | No. 1 or No. 2
Fuel Specification |  | ASTM D396-76 |  | ASTM D396-76
Fuel Sulfur Content (%) | 0.5% | 0.005 |  | 0.5
Control Technology
Operating Hours Limit |  | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period. |  | Calculated monthly as the sum of each consecutive 12-month period.
Allowed Operating Modes
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ
GENERATOR SET 2
Reference Number | 2 | 2 | 2 | Ref No. 2
Number of Generators | 1 | 1 | 1 | 1
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model |  |  | 1500 kW diesel-powered emergency generator
Rated Capacity (kW) | 1500 | 1500 | 1500 | 1500
Rated Capacity (BHP) |  | 2500 | 2500 | 2500
Rated Capacity (HP) | 2500
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Distillate oil | distillate oil | distillate oil | distillate oil
Secondary Fuel Type | Distillate oil
Fuel Grade |  | numbers 1 or 2 fuel oil |  | No. 1 or No. 2
Fuel Specification |  | ASTM D396-76 |  | ASTM 0396-76
Fuel Sulfur Content (%) | 0.5% | 0.005 |  | 0.5
Control Technology
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period. |  | Consecutive 12-month period; calculated monthly (sum of hours over each consecutive 12-month period).
Allowed Operating Modes
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes |  | Yes
MACT Subpart ZZZZ
GENERATOR SET 3
Reference Number | Yes | 1 | 1 | Ref No. 1
Number of Generators | Yes | 1 | 1 | 1
Included in Project |  | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model |  |  | 1500 kW diesel-powered emergency generator
Rated Capacity (kW) | 1500 | 1500 | 1500 | 1500
Rated Capacity (BHP) |  | 2500 | 2500 | 2500
Rated Capacity (HP) | 2500
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Distillate oil | distillate oil | distillate oil | distillate oil
Secondary Fuel Type
Fuel Grade | 1 or 2 | numbers 1 or 2 fuel oil
Fuel Specification |  | ASTM D396-76 |  | ASTM 0396-76
Fuel Sulfur Content (%) | 0.5% | 0.005 |  | 0.5
Control Technology
Operating Hours Limit |  | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period. |  | Consecutive 12-month period, calculated monthly as the sum of each consecutive 12-month period.
Allowed Operating Modes
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ

## Virginia_11790
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number | 11790 | 11790 | 11790 | 11790
Permit Issuance Date | 2016-08-23 | 2016-08-23 | 2016-08-23 | 2016-08-23
Permit Expiration Date
Facility Name | DP Facilities Inc. South, LLC | DP Facilities Inc. South, LLC | DP Facilities Inc. South, LLC | DP Facilities Inc. South, LLC
Facility Address | 5978 Windswept BLVD, Wise, VA 24293 | 5978 Windswept Blvd Wise, VA 24293 | 5978 Windswept Blvd, Wise, VA 24293 | 5978 Windswept Blvd
Facility County | Wise County | Wise County | Wise County | Wise County
Facility State |  | VA |  | VA
Construction Notification Required
Construction Notification Window (Days)
Startup Notification Required
Startup Notification Window (Days)
Permit Copy Onsite Required |  | Yes |  | Yes
Right of Entry Clause |  | The permittee shall allow authorized local, state, and federal representatives, upon the presentation of credentials: a. To enter upon the permittee's premises on which the facility is located or in which any records are required to be kept under the terms and conditions of this permit; b. To have access to and copy at reasonable times any records required to be kept under the terms and conditions of this permit or the State Air Pollution Control Board Regulations; c. To inspect at reasonable ti... |  | 15. Rl^ht^Entry-The permittee shall allow authorized local, state, and federal represented^ upon tbe presentation of credentials: a. Toenter upon the permittee's premises on which the facility is located or in which anv records are required to be kept undertbe terms and conditions oftbis permit: b. Tohave access to and copy at reasonable times any records required to be kept underthe terms and conditions oftbis permit ortbe State Air Follution Control Board Regulations: c. Toinspect at reasonabl...
GENERATOR SET 1
Reference Number | EG01-EG06 | EG01 - EG06 | EG01 - EG06 | EG01–EG06
Number of Generators | 6 | 6 | 6 | 6
Included in Project | Yes | Yes |  | Yes
Make | Cummins | Cummins | Cummins | Cummins
Model | QSK78-G12 | QSK78-G12 | QSK78-G12 | QSK78-G12
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) |  |  | 4060
Rated Capacity (HP) | 4060 | 4060
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel | diesel fuel | diesel fuel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 | S15 diesel fuel oil
Fuel Specification |  | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015 |  | 0.0015
Control Technology | “controlled by turbocharged engines, charge air coolers, and the use of good operating practices and performing appropriate maintenance in accordance with the manufacturer recommendations.” | turbocharged engines, charge air coolers, and the use of good operating practices and performing appropriate maintenance in accordance with the manufacturer recommendations. | Turbocharged engines and charge air coolers, plus good operating practices and maintenance per manufacturer recommendations
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12 month period |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated each month by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural disaster, or severe weather conditions. b. For periodic maintenance, testing, and operational training. |  | Emergency operation during sudden and reasonably unforeseeable events that disrupt or disconnect the primary power source beyond the owner/operator’s control (e.g., electrical grid failure; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather conditions); and operation for periodic maintenance, testing, and operational training.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | not less than once each month in which the unit is operated |  | not less than once each month in which the unit is operated
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes |  | Yes
MACT Subpart ZZZZ |  | Yes |  | Yes
GENERATOR SET 2
Reference Number | EG07 | EG07 | EG07 | EG07
Number of Generators | Yes | 1 | 1 | 1
Included in Project |  | Yes |  | Yes
Make | Cummins | Cummins | Cummins | Cummins
Model | QSK19-G8 | QSK19-G8 | QSK19-G8 | QSK19-G8
Rated Capacity (kW) | 600 | 600 | 600 | 600
Rated Capacity (BHP) |  |  | 967
Rated Capacity (HP) | 967 | 967
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel | diesel fuel | diesel fuel | diesel fuel
Secondary Fuel Type | Diesel
Fuel Grade |  | S15 diesel fuel oil
Fuel Specification |  | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015 |  | 0.0015
Control Technology | “controlled by turbocharged engines, charge air coolers, and the use of good operating practices and performing appropriate maintenance in accordance with the manufacturer recommendations.” | turbocharged engines, charge air coolers, and the use of good operating practices and performing appropriate maintenance in accordance with the manufacturer recommendations. | Turbocharged engine and charge air cooler, plus good operating practices and maintenance per manufacturer recommendations
Operating Hours Limit |  | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12 month period |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated each month by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural disaster, or severe weather conditions. b. For periodic maintenance, testing, and operational training. |  | Emergency operation during sudden and reasonably unforeseeable events that disrupt or disconnect the primary energy or power source (including failure of the electrical grid; on-site disaster or equipment failure; and public service emergencies such as flood, fire, natural disaster, or severe weather conditions) and operation for periodic maintenance, testing, and operational training.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | not less than once each month in which the unit is operated |  | not less than once each month in which the unit is operated.
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes |  | Yes
MACT Subpart ZZZZ |  | Yes |  | Yes

## Virginia_41064
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number | 41064 | 41064 | 41064 | 41064
Permit Issuance Date | 2018-08-10 | 2018-08-10 | 2018-08-16 | 2018-08-10
Permit Expiration Date
Facility Name | Equinix | Equinix | Equinix | Equinix
Facility Address | 18155 Technology Drive Culpeper, VA 22701 | 18155 Technology Drive, Culpeper, VA 22701 | 18155 Technology Drive, Culpeper, VA 22701 | 18155 Technology Drive
Facility County | Culpeper County | Culpeper County | Culpeper County | Culpeper County
Facility State | VA | VA |  | VA
Construction Notification Required |  |  |  | Yes
Construction Notification Window (Days) |  |  |  | 80
Startup Notification Required |  |  |  | Yes
Startup Notification Window (Days) |  |  |  | 15
Permit Copy Onsite Required |  |  |  | Yes
Right of Entry Clause |  |  |  | 24. Right of Entry^The permittee shall allow authorized lor^l, state, and federal represented^ upon tbe presented a. Toenter upon the permittee's premises on which the facility is located or in which any records are required to be kept underthe terms and conditions ofthis permit; b. Tohave access to and copy at reasonable times any records required to be kept underthe terms and conditions ofthispermitortheStateAirPollution Control Soard Regulations; c. Toinspect at reasonable times any...
GENERATOR SET 1
Reference Number | DCD-D, DCD-E, DCD-R | DCD-D, DCD-E, DCD-R | DCD-D, DCD-E, DCD-R | DCD-D
Number of Generators | 3 | 3 | 3 | 1
Included in Project | Yes | Yes
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | 3516C-HD | 3516C-HD | 3516C-HD | 3516C-HD
Rated Capacity (kW) | 2500 | 2500 | 2500
Rated Capacity (BHP) |  |  | 3634
Rated Capacity (HP) | 3634 | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate) | ultra low sulfur diesel fuel
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15 |  | ultra low sulfur 2-D or 2-D S15
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015
Control Technology | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR)
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period. |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated by adding the most recently completed calendar month to the totals for the preceding eleven months.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ... |  | Emergency power generation due to failure or loss of primary electrical service beyond the facility’s reasonable control (allowed while service is unavailable); ISO-declared emergency participation in an ISO Emergency Load Response Program (limited to 60 hours per generator per calendar year, with notification to DEQ after contracting); Critical Power Generation for loss or anticipated loss of acceptable power beyond the facility’s reasonable control (allowed until acceptable service is restored...
Opacity Limit (%) |  | 5
Hour Meter Required |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years) |  |  |  | 2
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 2
Reference Number | DCA-A through DCA-E and DCA-Swing | DCA-A through DCA-E and DCA-Swing | DCA-A through DCA-E and DCA-Swing | DCD-E
Number of Generators | 6 | 6 | 6 | 1
Included in Project | No | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | 3516BTA | 3516BTA | 3516B TA | 3516C-HD
Rated Capacity (kW) | 2250 | 2250 | 2250
Rated Capacity (BHP) |  |  | 3286
Rated Capacity (HP) | 3286 | 3286
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate) | ultra low sulfur diesel fuel
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15 |  | 2-D S15
Fuel Specification | ASTM D975 | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015
Control Technology | N/A | N/A | N/A
Operating Hours Limit | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period. |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month's hours to the totals for the preceding eleven months.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ... |  | Emergency power generation during utility failure beyond the facility’s control; ISO-declared emergency participation in an ISO Emergency Load Response Program (up to 60 hours per generator per calendar year); Critical Power Generation for loss or anticipated loss of acceptable power service beyond the facility’s control; Alternate Power Generation (voluntary peak-shaving, demand response, or interruptible power supply arrangements) for SCR-equipped units only when urea injection can be sustaine...
Opacity Limit (%) |  | 5 |  | 5
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service. |  | once per day during each test firing and during days in which the engine generator sets are called into service
Recordkeeping Window (Years)
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 3
Reference Number | DCB-A through DCB-F | DCB-A through DCB-F | DCB-A through DCB-F | DCD-R
Number of Generators | 6 | 6 | 6
Included in Project | No | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3516C DITA | 3516C DITA | 3516C DITA | 3516C-HD
Rated Capacity (kW) | 2500 | 2500 | 2500
Rated Capacity (BHP) |  |  | 3634
Rated Capacity (HP) | 3634 | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate) | ultra low sulfur diesel fuel
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | SCR-Endure Systems | SCR-Endure Systems | SCR-Endure Systems
Operating Hours Limit | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ...
Opacity Limit (%) |  | 5
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service. |  | shall be observed by the permittee at a minimum frequency of once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years)
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 4
Reference Number | DCB-G through DCB-H | DCB-G through DCB-H | DCB-G through DCB-H | DCA-A through DCA-E
Number of Generators | 2 | 2 | 2
Included in Project | No | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3512C-HD | 3512C-HD | 3512C-HD | 3516BTA
Rated Capacity (kW) | 1500 | 1500 | 1500 | 2250
Rated Capacity (BHP) |  |  | 2206
Rated Capacity (HP) | 2206 | 2206
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate) | ultra low sulfur diesel fuel
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15 |  | 2-D, 2-D S15
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR)
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period. |  | Consecutive 12-month rolling period, calculated monthly by adding the most recent calendar month’s total to the prior eleven months.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ...
Opacity Limit (%) |  | 5
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service. |  | at a minimum frequency of once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years)
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 5
Reference Number | DCC-A through DCC-D | DCC-A through DCC-D | DCC-A through DCC-D | DCA-Swing
Number of Generators | 4 | 4 | 4
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3516C DITA | 3516C DITA | 3516C DITA
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2250
Rated Capacity (BHP) |  |  | 3634
Rated Capacity (HP) | 3634 | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate)
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015
Control Technology | SCR-Endure Systems | SCR-Endure Systems | SCR-Endure Systems
Operating Hours Limit | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period. |  | Consecutive 12-month period, calculated monthly by adding the most recently completed month to the preceding eleven months.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ...
Opacity Limit (%) |  | 5 |  | 5
Hour Meter Required |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 6
Reference Number | DCC-E through DCC-F | DCC-E through DCC-F | DCC-E through DCC-F | DCB-A through DCB-F
Number of Generators | 2 | 2 | 2
Included in Project | No | No |  | No
Make | MTU | MTU | MTU | Caterpillar
Model | 12V4000G43 | 12V4000G43 | 12V4000 G43 Model 1500RXC6DT2
Rated Capacity (kW) | 1500 | 1500 | 1500
Rated Capacity (BHP) |  |  | 2039
Rated Capacity (HP) | 2039 | 2039
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate)
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15
Fuel Specification | ASTM D975 | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015
Control Technology | AirClarityTM 1500 SCR Systems | AirClarityTM 1500 SCR Systems | AirClarityTM 1500 SCR Systems
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period. |  | Consecutive 12-month rolling period, calculated monthly by adding the most recently completed calendar month to the preceding eleven months.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ... |  | Emergency operation during a utility power failure beyond the facility’s reasonable control; ISO‑declared emergency participation (Emergency Load Response Program), limited to 60 hours per generator per calendar year with required notification; critical power generation during a loss or anticipated loss of acceptable utility power beyond the facility’s reasonable control; and periodic maintenance, testing, and operational training.
Opacity Limit (%) |  | 5 |  | 5
Hour Meter Required |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years) |  |  |  | 2
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 7
Reference Number | DCD-A through DCD-C | DCD-A through DCD-C | DCD-A through DCD-C | DCB-G through DCB-H
Number of Generators | 3 | 3 | 3
Included in Project | No | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | 3516C-HD | 3516C-HD | 3516C-HD | 3512C-HD
Rated Capacity (kW) | 2500 | 2500 | 2500
Rated Capacity (BHP) |  |  | 3634
Rated Capacity (HP) | 3634 | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low sulfur diesel fuel | ultra low sulfur diesel fuel | ultra low sulfur diesel (no. 2 distillate)
Secondary Fuel Type
Fuel Grade | grade ultra low sulfur 2-D or grade 2-D S15 | grade ultra low sulfur 2-D or grade 2-D S15 |  | Grade ultra low sulfur 2-D or Grade 2-D S15
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR) | Caterpillar CAT® Selective Catalytic Reduction (SCR)
Operating Hours Limit | 500 | 500 | 500
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive twelve month period.
Allowed Operating Modes |  | Emergency; ISO-Declared Emergency (operations under this scenario shall not exceed 60 hours per generator each calendar year); Critical Power Generation; Alternate Power Generation for units equipped with a selective catalytic reduction system (Ref No's DCB-A through DCB-H, DCC-A through DCC-F, DCD-A through DCD-E, and DCD-R) for peak-shaving, demand response, or as part of an interruptible power supply arrangement when operating at a load level necessary to sustain urea injection as defined in ... |  | Emergency power generation during failure or loss of primary electrical power beyond the facility’s reasonable control (for the duration of the outage); ISO-declared emergency participation in an Independent System Operator’s Emergency Load Response Program (ELRP) (limited to 60 hours per generator per calendar year, with DEQ notification within 30 days of contract signing); Critical power generation during a loss or anticipated loss of acceptable electrical power from the primary provider beyon...
Opacity Limit (%) |  | 5 |  | 5
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | once per day during each test firing and during days in which the engine generator sets are called into service. |  | at a minimum frequency of once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years)
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 8
Reference Number | DCD-A through DCD-C |  |  | DCC-A through DCC-D
Number of Generators | 3 |  |  | 4
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | 3516C-HD
Rated Capacity (kW) | 2500 |  |  | 2500
Rated Capacity (BHP)
Rated Capacity (HP) | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15
Secondary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15
Fuel Grade |  |  |  | 2-D S15
Fuel Specification
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | CAT Selective Catalytic Reduction
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  |  |  | Emergency (utility power failure beyond the facility’s control) for the duration of the outage, after which operation may continue only under Critical Power Generation; ISO-declared emergency (participation in an Independent System Operator’s Emergency Load Response Program) up to 60 hours per generator per calendar year with notification to DEQ NRO within 30 days of contract; Critical Power Generation (loss or anticipated loss of acceptable power beyond the facility’s control) until acceptable ...
Opacity Limit (%) |  |  |  | 5
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years)
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 9
Reference Number | DCD-A through DCD-C |  |  | DCC-E through DCC-F
Number of Generators | 3
Included in Project
Make | Caterpillar |  |  | MTU
Model | 3516C-HD
Rated Capacity (kW) | 2500 |  |  | 1500
Rated Capacity (BHP)
Rated Capacity (HP) | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15 |  |  | ultra low sulfur diesel fuel
Secondary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | CAT Selective Catalytic Reduction
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by summing the most recent completed calendar month with the preceding eleven months.
Allowed Operating Modes |  |  |  | Emergency; ISO-declared emergency (participation in an ISO Emergency Load Response Program, limited to 60 hours per generator per calendar year with required DEQ notification upon contract); Critical Power Generation (loss or anticipated loss of acceptable electrical power beyond the facility’s control, until acceptable service is restored or no longer anticipated); Alternate Power Generation for SCR-equipped units (voluntary peak-shaving, demand response, or interruptible power supply, only whe...
Opacity Limit (%)
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | at a minimum frequency of once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years) |  |  |  | 2
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 10
Reference Number | DCD-A through DCD-C |  |  | DCD-A through DCD-C
Number of Generators | 3 |  |  | 3
Included in Project
Make | Caterpillar
Model | 3516C-HD
Rated Capacity (kW) | 2500
Rated Capacity (BHP)
Rated Capacity (HP) | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15 |  |  | ultra low sulfur diesel fuel
Secondary Fuel Type | ultra low-sulfur diesel 2-D, 2-D S15
Fuel Grade |  |  |  | 2-D S15
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | CAT Selective Catalytic Reduction
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  |  |  | Emergency power generation due to failure or loss of primary electrical power beyond the facility’s reasonable control (for the duration of the outage); ISO-declared emergency participation in an Independent System Operator’s Emergency Load Response Program (limited to 60 hours per generator per calendar year, with DEQ notification within 30 days of signing a participation contract); Critical Power Generation due to loss or anticipated loss of acceptable electrical power beyond the facility’s re...
Opacity Limit (%) |  |  |  | 5
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | at a minimum frequency of once per day during each test firing and during days in which the engine generator sets are called into service.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ

## Virginia_51232
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number | 51232 | 51232 | 51232 | 51232
Permit Issuance Date | 2024-06-24 00:00:00 | 2024-06-24 | 2024-06-24 | 2024-06-24
Permit Expiration Date
Facility Name | Quality Investment Properties Richmond, LLC | Quality Investment Properties Richmond, LLC | Quality Investment Properties Richmond, LLC
Facility Address | 6000 Technology Blvd Sandston, VA 23150 | 6000 Technology Boulevard, Sandston, Virginia | 6000 Technology Blvd, Sandston, VA 23150 | 6000 Technology Boulevard, Sandston, Virginia
Facility County | Henrico County | Henrico County | Henrico County | Henrico County
Facility State |  | VA |  | VA
Construction Notification Required |  |  |  | Yes
Construction Notification Window (Days) |  |  |  | 30
Startup Notification Required
Startup Notification Window (Days) |  |  |  | 15
Permit Copy Onsite Required |  |  |  | Yes
Right of Entry Clause |  |  |  | 42. Right of Entry - The permittee shall allow authorized local, state, and federal representatives, upon the presentation of credentials: a. To enter upon the permittee's premises on which the facility is located or in which any records are required to be kept under the terms and conditions of this permit; b. To have access to and copy at reasonable times any records required to be kept under the terms and conditions of this permit or the State Air Pollution Control Board Reg...
GENERATOR SET 1
Reference Number | EG77–EG79 | EG77–EG79 | EG77-EG79 | EG77–EG79
Number of Generators | 3 | 3 | 3 | 3
Included in Project | Yes | Yes |  | Yes
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C | CAT 3516C | CAT 3516C | 3516C
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) | 3674 | 3674 | 3674 | 3674
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly as the sum of each consecutive 12-month period; compliance demonstrated monthly by adding the most recently completed month to the prior 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation due to sudden and reasonably unforeseeable events disrupting the primary power source (including electrical grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (including abnormal system conditions requiring action to maintain frequency or prevent loss of firm load/equipment damage/tripping; capacity deficiency or excess; fuel shortage r...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 2
Reference Number | EG04–EG05 | EG04–EG05 | EG04-EG05 | EG04–EG05
Number of Generators | 2 | 2 | 2 | 2
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516 DITA | CAT 3516 DITA | CAT 3516 DITA | CAT 3516 DITA
Rated Capacity (kW) | 1825 | 1825 | 1825 | 1825
Rated Capacity (BHP) | 2588 | 2588 | 2588 | 2588
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period calculated monthly; compliance demonstrated by adding the most recently completed calendar month to the prior 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency situations where the primary power source is disrupted due to conditions beyond the owner/operator’s control (including grid failure, on-site disaster/equipment failure, or public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions to maintain reliability, capacity deficiency/excess, fuel shortages requiring departure from normal procedures, abnormal natural/man-made events requiring conse...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 3
Reference Number | EG06–EG07 | EG06–EG07 | EG06-EG07 | EG06–EG07
Number of Generators | 2 | 2 | 2 | 2
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C TA | CAT 3516C TA | CAT 3516C TA | 3516C TA
Rated Capacity (kW) | 2000 | 2000 | 2000 | 2000
Rated Capacity (BHP) | 2937 | 2937 | 2937 | 2937
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation due to sudden, unforeseeable events beyond the owner/operator’s control (including failure of the electrical grid; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions, capacity deficiency or excess, fuel shortage requiring conservative operations, abnormal natural or man-made threats requiring conservative operations, or abnorm...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 4
Reference Number | EG08–EG17 | EG08–EG17 | EG08-EG17 | EG08–EG17
Number of Generators | 10 | 10 | 10 | 10
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C | CAT 3516C | CAT 3516C | 3516C
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) | 3634 | 3634 | 3634 | 3634
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period calculated monthly, with compliance demonstrated by summing the most recently completed calendar month and the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency situations (failure of the electrical grid; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, severe weather); participation in an ISO-declared emergency; periodic maintenance, testing, and operational training. Non-emergency (alternate) power generation is only allowed after submitting documentation to DEQ and receiving DEQ approval to change the method of operation.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 5
Reference Number | EG18–EG34 | EG18–EG34 | EG18-EG34 | EG18–EG34
Number of Generators | 17 | 17 | 17 | 17
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C | CAT 3516C | CAT 3516C | 3516C
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) | 3634 | 3634 | 3634 | 3634
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance is demonstrated each month by adding the total for the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation (sudden and reasonably unforeseeable events disrupting the primary energy/power source, including electrical grid failure; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather), participation in an ISO-declared emergency, and periodic maintenance, testing, and operational training; any change to non-emergency (alternate) power generation requires prior DEQ approval.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 6
Reference Number | EG35–EG43 | EG35–EG43 | EG35-EG43 | EG35–EG43
Number of Generators | 9 | 9 | 9 | 9
Included in Project | No | No |  | No
Make | MTU | MTU | MTU | MTU
Model | 20V4000 DS2500 | 20V4000 DS2500 | 20V4000 DS2500 | 20V4000 DS2500
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) | 3674 | 3674 | 3674 | 3674
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period; calculated monthly as the sum of the last 12 months, with compliance demonstrated monthly by adding the most recent month to the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation (including grid failure, onsite disaster/equipment failure, and public service emergencies), participation in ISO-declared emergencies, and periodic maintenance, testing, and operational training; non-emergency (alternate) power generation only with prior DEQ approval.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 7
Reference Number | EG44–EG77 | EG44–EG77 | EG44-EG77 | EG44–EG76
Number of Generators | 33 | 33 | 33
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C | CAT 3516C | CAT 3516C | 3516C
Rated Capacity (kW) | 2500 | 2500 | 2500 | 2500
Rated Capacity (BHP) | 3674 | 3674 | 3674 | 3674
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation due to sudden and reasonably unforeseeable disruption of the primary power source (including failure of the electrical grid, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; and periodic maintenance, testing, and operational training. Any change to non-emergency (alternate) power generation requires prior DEQ approval.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 8
Reference Number | EG80-EG112 | EG80-EG112 | EG80-EG112 | EG80–EG112
Number of Generators | 33 | 33 | 33 | 33
Included in Project | No | No |  | No
Make | MTU | MTU | MTU | MTU
Model | 16V4000 DS2250 | 16V4000 DS2250 | 16V4000 DS2250 | 16V4000 DS2250
Rated Capacity (kW) | 2250 | 2250 | 2250 | 2250
Rated Capacity (BHP) | 3350 | 3350 | 3350 | 3350
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by adding the most recently completed calendar month to the preceding 11 months (for the combined EG80–EG112 group).
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency situations where the primary energy/power source is disrupted beyond the owner/operator’s control (including electrical grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (as defined in the permit); and periodic maintenance, testing, and operational training. Any change to non-emergency (alternate) power generation requires prior DEQ approval.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 9
Reference Number | EG113-EG145 | EG113-EG145 | EG113-EG145 | EG113–EG145
Number of Generators | 33 | 33 | 33 | 33
Included in Project | No | No |  | No
Make | MTU | MTU | MTU | MTU
Model | 16V4000 DS2250 | 16V4000 DS2250 | 16V4000 DS2250 | 16V4000 DS2250
Rated Capacity (kW) | 2250 | 2250 | 2250 | 2250
Rated Capacity (BHP) | 3350 | 3350 | 3350 | 3350
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by summing the most recently completed calendar month plus the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency operation during sudden and reasonably unforeseeable loss of primary power (including grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions requiring action to maintain system reliability/safety, capacity deficiency or excess, fuel shortage requiring departure from normal procedures, abnormal natural events or man-made threats r...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 10
Reference Number | EG146-EG244 | EG146-EG244 | EG146-EG244 | EG146–EG244
Number of Generators | 99 | 99 | 99 | 99
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar or MTU | MTU
Model | CAT 3516C | CAT 3516C | CAT 3516C or MTU 16V4000 DS2250 or equivalent | 16V4000 DS2250
Rated Capacity (kW) | 2500 | 2500 | 0 | 2250
Rated Capacity (BHP) | 3634 | 3634 | 0 | 3350
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by adding the most recently completed calendar month to the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation (due to grid failure; on-site disaster or equipment failure; or public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions requiring action to maintain frequency or prevent loss of firm load/equipment damage; capacity deficiency or excess; fuel shortage requiring departure from normal procedures; abnormal natural events or man-made threats requiring conservative operations...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 11
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 | EG245
Number of Generators | 8 | 8 | 8 | 1
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT C32 | CAT C32 | CAT C32 | CAT C32
Rated Capacity (kW) | 1250 | 1250 | 1250 | 1250
Rated Capacity (BHP) | 1821 | 1821 | 1821 | 1821
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | turbocharged engine and aftercooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency power generation due to sudden and reasonably unforeseeable events beyond the owner’s control that disrupt or disconnect the primary power source (including electrical grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (as defined in the permit: abnormal system conditions requiring action to maintain reliability/safety; capacity deficiency/excess; fuel ...
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 12
Reference Number | EG246-EG280, EG282-EG316, EG318-EG352, EG354-EG391, EG393-EG430, EG432-EG469, EG471-EG508, EG510-EG547, | EG246-EG280, EG282-EG316, EG318-EG352, EG354-EG391, EG393-EG430, EG432-EG469, EG471-EG508, EG510-EG547, | EG246-EG280, EG282-EG316, EG318-EG352, EG354-EG391, EG393-EG430, EG432-EG469, EG471-EG508, EG510-EG547 | EG281
Number of Generators | 295 | 295 | 295 | 1
Included in Project | No | No |  | No
Make | Caterpillar | Caterpillar | Caterpillar | Caterpillar
Model | CAT 3516C | CAT 3516C | CAT 3516C | CAT C32
Rated Capacity (kW) | 2500 | 2500 | 2500 | 1250
Rated Capacity (BHP) | 3633 | 3633 | 3633 | 1821
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel | diesel fuel | diesel | diesel fuel
Secondary Fuel Type
Fuel Grade | S15 diesel fuel oil | S15 diesel fuel oil
Fuel Specification | ASTM D975 | ASTM D975 |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015 | 0.0015 |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler | turbocharged engine and aftercooler | Good operating practices and maintenance; turbocharged engine and aftercooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  | Emergency Power Generation - The engine-generator sets (Ref. Nos. EG04-EG547) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, ... |  | Emergency situations (including grid failure, on-site disaster/equipment failure, and public service emergencies), participation in ISO-declared emergencies, periodic maintenance, testing, and operational training; non-emergency (alternate) power generation only if documentation is submitted and DEQ approval is received for a change in method of operation.
Opacity Limit (%) |  | 10 |  | 10
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | with a frequency of not less than once each day the engine-generator set is operated. |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 13
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG317
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period, calculated monthly as the sum of each consecutive 12-month period; compliance demonstrated monthly by adding the most recently completed calendar month to the preceding 11 months.
Allowed Operating Modes |  |  |  | Operation is allowed only in: (a) emergencies arising from sudden, reasonably unforeseeable disruptions of the primary power source beyond the owner/operator’s control (including grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); (b) participation in an ISO-declared emergency (abnormal system conditions requiring action to maintain reliability or safety, capacity deficiency/excess, fuel shortage requiring...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 14
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG353
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period calculated monthly; compliance is demonstrated each month by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency operation when the primary power source is disrupted beyond the owner/operator's control (including grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (as defined in the permit); and periodic maintenance, testing, and operational training. Operation as non-emergency (alternate) power generation is prohibited unless DEQ approves a change in method of ope...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 15
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG392
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period, calculated monthly as a rolling sum: compliance is demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency operation due to disruption of the primary power source beyond the owner's control (including grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; periodic maintenance, testing, and operational training; non-emergency (alternate) power generation only after submitting documentation to and receiving approval from DEQ to change the method of operation.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 16
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG431
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | CAT C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly as the sum of each consecutive 12-month period; compliance demonstrated by adding the most recently completed month to the prior 11 months.
Allowed Operating Modes |  |  |  | Emergency situations (grid failure; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; and periodic maintenance, testing, and operational training. Any change to non-emergency (alternate) power generation requires prior DEQ approval.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 17
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG470
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | CAT C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly by adding the most recently completed calendar month to the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency operation due to sudden unforeseeable events disrupting primary power (including grid failure; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; and periodic maintenance, testing, and operational training. Non-emergency (alternate) power generation is only allowed if DEQ approves a documented change in the method of operation.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 18
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG509
Number of Generators | 3 |  |  | 1
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | C32
Rated Capacity (kW) | 1250 |  |  | 1250
Rated Capacity (BHP) |  |  |  | 1821
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance is demonstrated by adding the most recent completed calendar month to the totals from the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency power generation (sudden, unforeseeable disruption of the primary power source beyond the owner/operator’s control, including grid failure; on-site disaster or equipment failure; and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in ISO-declared emergencies (as defined in the permit); and periodic maintenance, testing, and operational training. Non-emergency (alternate) power generation is only allowed if DEQ approves a change in the...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 19
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG246–EG280
Number of Generators | 3 |  |  | 35
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | CAT 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the preceding 11 months’ totals.
Allowed Operating Modes |  |  |  | Emergency operation during sudden unforeseeable power disruptions (grid failure, on-site disaster or equipment failure, or public service emergencies such as flood, fire, natural disaster, severe weather); participation in an ISO-declared emergency; and periodic maintenance, testing, and operational training. Non-emergency (alternate) operation is not allowed unless DEQ approves a change in the method of operation.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 20
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG282–EG316
Number of Generators | 3 |  |  | 35
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly as the sum of each consecutive 12-month period; compliance demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency operation due to sudden and reasonably unforeseeable events that disrupt or disconnect the primary power source (including electrical grid failure, on-site disaster or equipment failure, and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions requiring action to maintain reliability/safety, capacity deficiency or excess, fuel shortage requiring departure from normal procedures, abno...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 21
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG318–EG352
Number of Generators | 3
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Operation is limited to: (a) emergencies arising from sudden and reasonably unforeseeable events that disrupt or disconnect the primary energy/power source beyond the owner/operator's control (including failure of the electrical grid; on-site disaster or equipment failure; and public service emergencies such as flood, fire, natural disaster, or severe weather); (b) participation in an ISO-declared emergency (including abnormal system conditions requiring action to maintain system frequency, prev...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 22
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG354–EG391
Number of Generators | 3
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated each month by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency power generation when the primary power/energy source is disrupted due to conditions beyond the owner/operator’s control (e.g., electrical grid failure; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (abnormal system conditions requiring action to maintain reliability/safety; capacity deficiency or excess; fuel shortage requiring departure from normal procedures; abn...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 23
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG393–EG430
Number of Generators | 3 |  |  | 38
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | CAT 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated each month by adding the most recent completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency situations (sudden and reasonably unforeseeable disruptions beyond the owner/operator's control, including failure of the electrical grid; on-site disaster or equipment failure; or public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; and periodic maintenance, testing, and operational training. Non-emergency (alternate) power generation is allowed only after submitting documentation to DEQ and receiving DEQ app...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 24
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG432–EG469
Number of Generators | 3
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period, calculated monthly by summing the most recently completed calendar month with the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency operation due to sudden and reasonably unforeseeable disruption of the primary power source (including failure of the electrical grid; on-site disaster or equipment failure; public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency; periodic maintenance, testing, and operational training. Non-emergency (alternate) power generation is allowed only with prior DEQ approval of a change in method of operation.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 25
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG471–EG508
Number of Generators | 3 |  |  | 38
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | CAT 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the previous 11 months.
Allowed Operating Modes |  |  |  | Emergency power generation (including grid failure, on-site disaster/equipment failure, and public service emergencies such as flood, fire, natural disaster, severe weather); participation in ISO-declared emergencies; periodic maintenance, testing, and operational training; non-emergency (alternate) power generation only after submitting documentation and receiving DEQ approval for the change in method of operation.
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ
GENERATOR SET 26
Reference Number | EG245, EG281, EG317, EG353, EG392, EG431, EG470, EG509 |  |  | EG510–EG547
Number of Generators | 3
Included in Project |  |  |  | No
Make | Caterpillar |  |  | Caterpillar
Model | CAT C32 |  |  | 3516C
Rated Capacity (kW) | 1250 |  |  | 2500
Rated Capacity (BHP) |  |  |  | 3633
Rated Capacity (HP) | 1821
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | diesel fuel s15 |  |  | diesel fuel
Secondary Fuel Type | diesel fuel s15
Fuel Grade
Fuel Specification |  |  |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% |  |  | 0.0015
Control Technology | good pracitce, manufacture specs, and turbocharged engine and after-cooler
Operating Hours Limit
Operating Hours Rolling Window |  |  |  | Consecutive 12-month rolling period, calculated monthly; compliance demonstrated monthly by adding the most recently completed calendar month to the totals for the preceding 11 months.
Allowed Operating Modes |  |  |  | Emergency power generation due to sudden and reasonably unforeseeable disruptions of the primary power source (including failure of the electrical grid; on-site disaster or equipment failure; and public service emergencies such as flood, fire, natural disaster, or severe weather); participation in an ISO-declared emergency (including abnormal system conditions requiring action to maintain reliability or safety; capacity deficiency or excess; fuel shortage requiring departure from normal procedur...
Opacity Limit (%) |  |  |  | 10
Hour Meter Required |  |  |  | Yes
Observation Frequency |  |  |  | with a frequency of not less than once each day the engine-generator set is operated.
Recordkeeping Window (Years) |  |  |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ

## Illinois_031440ANI_08010054_IL_
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number |  | 031440ANI
Permit Issuance Date |  | 2018-08-15
Permit Expiration Date |  | 2028-08-15
Facility Name |  | Equinix LLC
Facility Address |  | 1905 Lunt Avenue, Elk Grove Village, Cook County, 60007
Facility County |  | Cook County
Facility State |  | IL
Construction Notification Required
Construction Notification Window (Days)
Startup Notification Required |  | No
Startup Notification Window (Days)
Permit Copy Onsite Required
Right of Entry Clause
GENERATOR SET 1
Reference Number |  | EGA1, EGA2, EGAR, EGA3, EGA4, EGB1, EGB2, EGBR, EGB3, EGB4, EGC1, EGC2, EGCR, EGSS, and EGSN
Number of Generators |  | 15
Included in Project
Make
Model
Rated Capacity (kW) |  | 2500
Rated Capacity (BHP)
Rated Capacity (HP) |  | 3634
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | distillate oil
Secondary Fuel Type
Fuel Grade |  | Grades No. 1 and 2 (i.e., diesel)
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | running 12 month total
Allowed Operating Modes |  | In order for the engine to be considered an emergency stationary ICE under 40 CFR 60 Subpart IIII, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in 40 CFR 60.4211(f)(1) through (3), is prohibited.
Opacity Limit (%) |  | 30
Hour Meter Required |  | Yes
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 2
Reference Number |  | EGC5 – EGC8
Number of Generators |  | 4
Included in Project
Make
Model
Rated Capacity (kW) |  | 2500
Rated Capacity (BHP)
Rated Capacity (HP) |  | 3633
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | distillate oil
Secondary Fuel Type
Fuel Grade |  | Grades No. 1 and 2 (i.e., diesel)
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 230
Operating Hours Rolling Window |  | running 12 month total
Allowed Operating Modes |  | In order for the engine to be considered an emergency stationary ICE under 40 CFR 60 Subpart IIII, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in 40 CFR 60.4211(f)(1) through (3), is prohibited.
Opacity Limit (%) |  | 30
Hour Meter Required |  | Yes
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes

## Illinois_031471AEN_21050040_IL_
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number |  | 21050040
Permit Issuance Date |  | 2021-10-04
Permit Expiration Date
Facility Name |  | Aligned Data Centers (ORD) Prop Co, LLC
Facility Address |  | 505 Northwest Ave, Northlake, Cook County, 60164
Facility County |  | Cook County
Facility State |  | IL
Construction Notification Required |  | Yes
Construction Notification Window (Days) |  | 30
Startup Notification Required |  | Yes
Startup Notification Window (Days) |  | 15
Permit Copy Onsite Required
Right of Entry Clause
GENERATOR SET 1
Reference Number |  | Forty-Nine (49) 3,000 kW (4,393 BHP) Diesel Emergency Generators
Number of Generators |  | 49
Included in Project |  | Yes
Make
Model
Rated Capacity (kW) |  | 3000
Rated Capacity (BHP) |  | 4393
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel oil
Secondary Fuel Type
Fuel Grade |  | No. 2
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 1793
Operating Hours Rolling Window |  | running 365 days total
Allowed Operating Modes |  | Pursuant to 40 CFR 60.4211(f), if you own or operate an emergency stationary ICE, you must operate the emergency stationary ICE according to the requirements in 40 CFR 60.4211(f)(1) through (3). In order for the engine to be considered an emergency stationary ICE under 40 CFR 60 Subpart IIII, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in 40 CFR 60.4211(f)(1) throug...
Opacity Limit (%) |  | 30
Hour Meter Required |  | Yes
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 2
Reference Number |  | Two (2) 500 kW (762 BHP) Diesel Emergency Generators
Number of Generators |  | 2
Included in Project |  | Yes
Make
Model
Rated Capacity (kW) |  | 500
Rated Capacity (BHP) |  | 762
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel oil
Secondary Fuel Type
Fuel Grade |  | No. 2
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 100
Operating Hours Rolling Window |  | running 365 days total
Allowed Operating Modes |  | Pursuant to 40 CFR 60.4211(f), if you own or operate an emergency stationary ICE, you must operate the emergency stationary ICE according to the requirements in 40 CFR 60.4211(f)(1) through (3). In order for the engine to be considered an emergency stationary ICE under 40 CFR 60 Subpart IIII, any operation other than emergency operation, maintenance and testing, emergency demand response, and operation in non-emergency situations for 50 hours per year, as described in 40 CFR 60.4211(f)(1) throug...
Opacity Limit (%) |  | 30
Hour Meter Required |  | Yes
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes

## Kentucky_F-23-031
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number |  | F-23-031
Permit Issuance Date |  | 2023-11-03
Permit Expiration Date |  | 2028-11-03
Facility Name |  | Cyrus One, LLC
Facility Address |  | 7190-7200 Industrial Road, Florence, KY 41042
Facility County |  | Boone
Facility State |  | KY
Construction Notification Required
Construction Notification Window (Days)
Startup Notification Required
Startup Notification Window (Days)
Permit Copy Onsite Required
Right of Entry Clause |  | the permittee shall allow authorized representatives of the Cabinet to perform the following during reasonable times: a. Enter upon the premises to inspect any facility, equipment (including air pollution control equipment), practice, or operation; b. To access and copy any records required by the permit; c. Sample or monitor, at reasonable times, substances or parameters to assure compliance with the permit or any applicable requirements. Reasonable times are defined as during all hours of op...
GENERATOR SET 1
Reference Number |  | 01A
Number of Generators |  | 1
Included in Project |  | No
Make |  | Caterpillar
Model |  | 3512
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 1676
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  | a. There is no time limit on the use of emergency stationary RICE emergency situations. [40 CFR 63.6640(f)(1)] b. The permittee may operate each of the engines for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with...
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ |  | No
GENERATOR SET 2
Reference Number |  | 01B
Number of Generators |  | 1
Included in Project |  | No
Make |  | Detroit
Model |  | T1637K36
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2550
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  | a. There is no time limit on the use of emergency stationary RICE emergency situations. [40 CFR 63.6640(f)(1)] b. The permittee may operate each of the engines for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with...
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ |  | No
GENERATOR SET 3
Reference Number |  | 01C
Number of Generators |  | 1
Included in Project |  | No
Make |  | Detroit
Model |  | T1637K36
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2550
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  | a. There is no time limit on the use of emergency stationary RICE emergency situations. [40 CFR 63.6640(f)(1)] b. The permittee may operate each of the engines for a maximum of 100 hours per calendar year for maintenance checks and readiness testing, provided that the tests are recommended by federal, state or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with...
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII
MACT Subpart ZZZZ |  | No
GENERATOR SET 4
Reference Number |  | 02A
Number of Generators |  | 1
Included in Project |  | Yes
Make |  | Cummins
Model |  | DFLE-57740008
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2220
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling total basis
Allowed Operating Modes
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly and 12-month rolling total basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 5
Reference Number |  | 02B
Number of Generators |  | 1
Included in Project |  | Yes
Make |  | Cummins
Model |  | DFLE-57740008
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2220
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling total basis
Allowed Operating Modes
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly and 12-month rolling total basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 6
Reference Number |  | 02C
Number of Generators |  | 1
Included in Project |  | Yes
Make |  | Cummins
Model |  | DFLE-57740008
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2220
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling total basis
Allowed Operating Modes
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly and 12-month rolling total basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 7
Reference Number |  | 02D
Number of Generators |  | 1
Included in Project |  | Yes
Make |  | Cummins
Model |  | DFLE-57740008
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2220
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling total basis
Allowed Operating Modes
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly and 12-month rolling total basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 8
Reference Number |  | 02E
Number of Generators |  | 1
Included in Project |  | Yes
Make |  | Cummins
Model |  | DFLE-57740008
Rated Capacity (kW)
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2220
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | Diesel
Secondary Fuel Type
Fuel Grade
Fuel Specification
Fuel Sulfur Content (%)
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling total basis
Allowed Operating Modes
Opacity Limit (%)
Hour Meter Required
Observation Frequency |  | monthly and 12-month rolling total basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes

## Michigan_112-17
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number |  | 112-17 |  | 112-17; P0243
Permit Issuance Date |  | 2017-08-21 |  | 2017-08-21
Permit Expiration Date
Facility Name |  | Beaumont Information Technology Center |  | Beaumont Information Technology Center
Facility Address |  | 1350 Stephenson Highway Troy, Michigan |  | 1350 Stephenson Highway
Facility County |  | Cakland |  | Cakland
Facility State |  | MI |  | MI
Construction Notification Required
Construction Notification Window (Days)
Startup Notification Required
Startup Notification Window (Days)
Permit Copy Onsite Required
Right of Entry Clause
GENERATOR SET 1
Reference Number |  | EU-GENP |  | EU-GENP
Number of Generators |  | 1 |  | 1
Included in Project |  | Yes |  | Yes
Make
Model
Rated Capacity (kW) |  | 1500
Rated Capacity (BHP)
Rated Capacity (HP) |  | 2205
Maximum Capacity (BHP)
Maximum Capacity (kW) |  | 1500
Primary Fuel Type |  | diesel fuel |  | diesel fuel
Secondary Fuel Type
Fuel Grade
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015 |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | 12-month rolling time period basis as determined at the end of each calendar month |  | 12-month rolling time period, determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate EU-GENP for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional hours to be used f... |  | Emergency operation; necessary maintenance checks and readiness testing (up to 100 hours per calendar year, with potential Department approval for additional hours or more if required by applicable standards); non-emergency operation (up to 50 hours per calendar year, counted toward the 100 hours for maintenance/testing, and not for peak shaving, demand response, or income generation except as provided in 40 CFR 60.4211(f)(3)(i)); all operation subject to a total cap of 500 hours per 12-month ro...
Opacity Limit (%) |  | 20 |  | 20
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  |  |  | on a monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes |  | Yes
MACT Subpart ZZZZ |  | Yes |  | Yes

## Michigan_PTI0000052
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number |  | PTI0000052 v1.0 |  | PTI0000052 v1.0
Permit Issuance Date |  | 2024-11-08 |  | 2024-11-08
Permit Expiration Date
Facility Name |  | Alliance Cloud Services, LLC |  | Alliance Cloud Services, LLC
Facility Address |  | 415 East Prairie Ronde Street Dowagiac, Michigan 49047 |  | 415 East Prairie Ronde Street
Facility County |  | Cass |  | Cass
Facility State |  | MI |  | MI
Construction Notification Required
Construction Notification Window (Days)
Startup Notification Required |  | Yes
Startup Notification Window (Days) |  | 30
Permit Copy Onsite Required
Right of Entry Clause
GENERATOR SET 1
Reference Number |  | EUGEN1 |  | EUGEN1-EUGEN15
Number of Generators |  | 1 |  | 15
Included in Project |  |  |  | Yes
Make
Model
Rated Capacity (kW) |  | 2000 |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015 |  | 0.15
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month |  | 12-month rolling time period, determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho... |  | Emergency operation; maintenance checks and readiness testing (up to 100 hours per calendar year per engine when recommended by specified entities, with additional hours allowed by petition or if required by applicable standards); and limited non-emergency operation (up to 50 hours per calendar year per engine, counted within the 100 hours for maintenance/testing, and not for peak shaving, non-emergency demand response, or income-generating power, except as provided in 40 CFR 60.4211(f)(3)(i)). ...
Opacity Limit (%) |  |  |  | 20
Hour Meter Required |  | Yes |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis |  | monthly and 12-month rolling
Recordkeeping Window (Years) |  | 5 |  | 5
NSPS Subpart IIII |  | Yes |  | Yes
MACT Subpart ZZZZ |  | Yes |  | Yes
GENERATOR SET 2
Reference Number |  | EUGEN2
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 3
Reference Number |  | EUGEN3
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 4
Reference Number |  | EUGEN4
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 5
Reference Number |  | EUGEN5
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 6
Reference Number |  | EUGEN6
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 7
Reference Number |  | EUGEN7
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 8
Reference Number |  | EUGEN8
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 9
Reference Number |  | EUGEN9
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 10
Reference Number |  | EUGEN10
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 11
Reference Number |  | EUGEN11
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 12
Reference Number |  | EUGEN12
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 13
Reference Number |  | EUGEN13
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 14
Reference Number |  | EUGEN14
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 15
Reference Number |  | EUGEN15
Number of Generators |  | 1
Included in Project
Make
Model
Rated Capacity (kW) |  | 2000
Rated Capacity (BHP)
Rated Capacity (HP)
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type |  | diesel fuel
Secondary Fuel Type
Fuel Grade |  | non-road diesel fuel
Fuel Specification |  | 40 CFR 80.510(b)
Fuel Sulfur Content (%) |  | 0.0015
Control Technology
Operating Hours Limit |  | 500
Operating Hours Rolling Window |  | per 12-month rolling time period as determined at the end of each calendar month
Allowed Operating Modes |  | The permittee may operate each engine in FGEMGENS for no more than 100 hours per calendar year for the purpose of necessary maintenance checks and readiness testing, provided that the tests are recommended by Federal, State, or local government, the manufacturer, the vendor, the regional transmission organization or equivalent balancing authority and transmission operator, or the insurance company associated with the engine. The permittee may petition the Department for approval of additional ho...
Opacity Limit (%)
Hour Meter Required |  | Yes
Observation Frequency |  | monthly and 12-month rolling time period basis
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes

## Virginia_52432
Field Name | Ground Truth | AQ Toolkit | LlamaExtract | Decision Tree | Notes
PERMIT DETAILS
Permit Number | 52432 | 52432 | 52432
Permit Issuance Date | 2025-07-07 00:00:00 | 2025-07-07 | 2025-07-07
Permit Expiration Date
Facility Name | Chirisa Richmond LLC | Chirisa Richmond LLC | Chirisa Richmond LLC
Facility Address | 1401 Meadowville Technology Pkway Chester, Virginia 23836 | 1401 Meadowville Technology Pkwy, Chester, Virginia 23836 | 1401 Meadowville Technology Pkwy, Chester, Virginia 23836
Facility County | Chesterfield County | Chesterfield County | Chesterfield County
Facility State |  | VA
Construction Notification Required |  | Yes
Construction Notification Window (Days) |  | 30
Startup Notification Required |  | Yes
Startup Notification Window (Days) |  | 15
Permit Copy Onsite Required |  | Yes
Right of Entry Clause |  | The permittee shall allow authorized local, state, and federal representatives, upon the presentation of credentials: To enter upon the permittee's premises on which the facility is located or in which any records are required to be kept under the terms and conditions of this permit; To have access to and copy at reasonable times any records required to be kept under the terms and conditions of this permit or the State Air Pollution Control Board Regulations; To inspect at reasonable times any f...
GENERATOR SET 1
Reference Number | EG07-EG15 | EG-2-01 through EG-2-31 | EG-2-01 through EG-2-31
Number of Generators | 31 | 31 | 31
Included in Project |  | Yes
Make | Caterpillar | Cummins | Cummins
Model | 3516C | C3000D6EB (QSK78-36) | C3000D6EB (QSK78-36)
Rated Capacity (kW) | 2500 | 3000 | 3000
Rated Capacity (BHP) |  | 4441 | 4441
Rated Capacity (HP) | 3633
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel (S15) | diesel fuel | diesel fuel
Secondary Fuel Type | Diesel (S15)
Fuel Grade |  | S15 diesel fuel oil
Fuel Specification |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015
Control Technology | Good operating practices and performing routine maintenance. | turbocharged engine and aftercooler/charge air cooler | turbocharged engine and aftercooler/charge air cooler; good operating practices and maintenance per manufacturer recommendations
Operating Hours Limit
Operating Hours Rolling Window
Allowed Operating Modes |  | The engine-generator sets (Ref. Nos. EG01 – EG15 and EG-2-01 through EG-2-31) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural...
Opacity Limit (%) |  | 10
Hour Meter Required |  | Yes
Observation Frequency |  | not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 2
Reference Number | EG07-EG15 | EG01-EG05 | EG01-EG05
Number of Generators | 31 | 5 | 5
Included in Project |  | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3516C | C175-16 | C175-16
Rated Capacity (kW) | 2500 | 3000 | 3000
Rated Capacity (BHP) |  | 4423 | 4423
Rated Capacity (HP) | 3633
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel (S15) | diesel fuel | diesel fuel
Secondary Fuel Type | Diesel (S15)
Fuel Grade |  | S15 diesel fuel oil
Fuel Specification |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015
Control Technology | Good operating practices and performing routine maintenance.
Operating Hours Limit |  | 150 | 150
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period.
Allowed Operating Modes |  | The engine-generator sets (Ref. Nos. EG01 – EG15 and EG-2-01 through EG-2-31) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural...
Opacity Limit (%) |  | 10
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 3
Reference Number | EG07-EG15 | EG06 | EG06
Number of Generators | 31 | 1 | 1
Included in Project |  | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3516C | 3512C | 3512C
Rated Capacity (kW) | 2500 | 1500 | 1500
Rated Capacity (BHP) |  | 2206 | 2206
Rated Capacity (HP) | 3633
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel (S15) | diesel fuel | diesel fuel
Secondary Fuel Type | Diesel (S15)
Fuel Grade |  | S15 diesel fuel oil
Fuel Specification |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015
Control Technology | Good operating practices and performing routine maintenance.
Operating Hours Limit |  | 150 | 150
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period.
Allowed Operating Modes |  | The engine-generator sets (Ref. Nos. EG01 – EG15 and EG-2-01 through EG-2-31) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural...
Opacity Limit (%) |  | 10
Hour Meter Required
Observation Frequency
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes
GENERATOR SET 4
Reference Number | EG07-EG15 | EG07-EG15 | EG07-EG15
Number of Generators | 31 | 9 | 9
Included in Project |  | No
Make | Caterpillar | Caterpillar | Caterpillar
Model | 3516C | 3516C | 3516C
Rated Capacity (kW) | 2500 | 2500 | 2500
Rated Capacity (BHP) |  | 3633 | 3633
Rated Capacity (HP) | 3633
Maximum Capacity (BHP)
Maximum Capacity (kW)
Primary Fuel Type | Diesel (S15) | diesel fuel | diesel fuel
Secondary Fuel Type | Diesel (S15)
Fuel Grade |  | S15 diesel fuel oil
Fuel Specification |  | ASTM D975
Fuel Sulfur Content (%) | 0.0015% | 0.0015
Control Technology | Good operating practices and performing routine maintenance. | turbocharged engine and aftercooler/charge air cooler | turbocharged engine and aftercooler/charge air cooler; good operating practices and maintenance per manufacturer recommendations
Operating Hours Limit |  | 150 | 150
Operating Hours Rolling Window |  | calculated monthly as the sum of each consecutive 12-month period.
Allowed Operating Modes |  | The engine-generator sets (Ref. Nos. EG01 – EG15 and EG-2-01 through EG-2-31) shall only be operated in the following modes: a. In situations that arise from sudden and reasonably unforeseeable events where the primary energy or power source is disrupted or disconnected due to conditions beyond the control of an owner or operator of a facility including: i. A failure of the electrical grid; ii. On-site disaster or equipment failure; or iii. Public service emergencies such as flood, fire, natural...
Opacity Limit (%) |  | 10
Hour Meter Required |  | Yes
Observation Frequency |  | not less than once each day the engine-generator set is operated
Recordkeeping Window (Years) |  | 5
NSPS Subpart IIII |  | Yes
MACT Subpart ZZZZ |  | Yes